## Sheet1
UCT002 Cell Densities and Voltages
Hydrometer
Battery | Cell | Voltage | Density (wt%) | Temperature (°C) | Notes / Observations
A01 | I | 2.189 | 42.3% | 23.6
| II | 2.184 | 42.8% | 23.6
| III | 2.176 | 42.6% | 23.3
| IV | 2.177 | 41% | 24.1
| V | 2.186 | 42.3% | 23.4
| VI | 2.179 | 43.1% | 23.5
A02 | I | 2.167 | 41.5% | 23.1
| II | 2.168 | 41% | 23.6
| III | 2.161 | 41.5% | 23.3
| IV | 2.156 | 40.4% | 23.4
| V | 2.164 | 40.8% | 23.3
| VI | 2.162 | 41% | 23.4
A03 | I | 2.131 | 36.3% | 22.5
| II | 2.145 | 39% | 22.5
| III | 2.133 | 33.3% | 22.8
| IV | 2.134 | 39.8% | 22.7
| V | 2.144 | 38.9% | 22.7
| VI | 2.141 | 38.6% | 22.8
A04 | I | 2.115 | 26.7% | 24.4
| II | 2.116 | 37.7% | 24.1
| III | 2.118 | 37.6% | 24.5
| IV | 2.112 | 37% | 24.4
| V | 2.113 | 37.1% | 24.2
| VI | 2.104 | 36.8% | 24.3
A05 | I | 2.078 | 31.8% | 24.1
| II | 2.096 | 35.6% | 24.2
| III | 2.08 | 33.6% | 24.8
| IV | 2.084 | 32.8% | 24.5
| V | 2.091 | 33.2% | 24.4
| VI | 2.085 | 33.2% | 24.1
A06 | I | 2.073 | 31.7% | 23.8
| II | 2.078 | 32.4% | 23.8
| III | 2.068 | 31.8% | 23.8
| IV | 2.067 | 31.2% | 23.9
| V | 2.07 | 31.7% | 24.2
| VI | 2.071 | 27.7% | 24.2
A07 | I | 2.039 | 27.9% | 23.8
| II | 2.049 | 28.6% | 24
| III | 2.036 | 27.7% | 23.9
| IV | 2.043 | 28.6% | 24.1
| V | 2.043 | 28.5% | 23.8
| VI | 2.038 | 27.7% | 23.9
A08 | I | 2.033 |  |  | Acid Sample Destroyed
| II | 2.033 | 26.8% | 23.6
| III | 2.024 | 26% | 23.8
| IV | 2.013 | 25.7% | 24.1
| V | 2.029 | 26.3% | 24
| VI | 2.038 | 27.6% | 24.3
A09 | I | 2 | 26.6% | 24.1
| II | 2.005 | 24.1% | 24
| III | 1.998 |  |  | Acid Sample Destroyed
| IV | 1.995 | 22.3% | 23.7
| V | 1.995 | 21% | 23.9
| VI | 1.99 | 21.2% | 23.4
A10 | I | 1.962 | 21.8% | 24.1
| II | 1.973 | 18.5% | 24.8
| III | 1.96 | 17% | 24.2
| IV | 1.95 | 27.8% | 24.1 | Batteries replaced at this point following low battery warning.
| V | 1.959 | 18.7% | 24.3
| VI | 1.966 | 17.7% | 24.1
B01 | I | 2.067 | 32.1% | 23.5 | Sample spilled but recovered from bench surface using pipette.
| II | 2.16 | 41.2% | 21.8 | Manually interpolated s.g. and T against standard data tables.
| III | 2.064 | 32.9% | 23
| IV | 2.14 | 28.1% | 23.2
| V | 2.158 | 40.7% | 23.5
| VI | 2.156 | 39.3% | 23.6
B02 | I | 2.144 | 39.1% | 23 | Red adhesive material in cell.
| II | 2.142 | 39.5% | 23.4
| III | 2.132 | 39.4% | 22 | Manually interpolated s.g. and T against standard data tables.
| IV | 2.145 | 39.6% | 23.3
| V | 2.146 | 40.6% | 23 | Cloudy Sample in density measurement.
| VI | 2.142 | 40.1% | 23.2 | Missing lead plates within grid of cell. Cloudy sample in desnity measurement.
B03 | I | 2.102 | 34.8% | 22.9
| II | 2.104 | 25.6% | 23.2
| III | 2.108 | 36.2% | 22 | Manually interpolated s.g. and T against standard data tables.
| IV | 2.105 | 35.9% | 23
| V | 2.105 | 36.1% | 23
| VI | 2.102 | 35.6% | 23.1
B04 | I | 2.079 | 32.3% | 23.1
| II | 2.083 | 34% | 23
| III | 2.08 | 33.3% | 22.9
| IV | 2.084 | 33.2% | 22.9
| V | 2.078 | 33.6% | 22.1 | Manually interpolated s.g. and T against standard data tables.
| VI | 2.082 | 33.4% | 22.8
B05 | I | 2.062 | 31.6% | 23 | Fine lead granes in sample at density measurement.
| II | 2.064 | 31.1% | 23
| III | 2.058 | 30.6% | 23
| IV | 2.058 | 31.1% | 22.8
| V | 2.06 | 30.5% | 22 | Manually interpolated s.g. and T against standard data tables.
| VI | 2.06 | 31.5% | 22.7
B06 | I | 2.041 | 27.6% | 23.1
| II | 2.047 | 29.4% | 23
| III | 2.047 | 28.8% | 22.9
| IV | 2.035 | 27.6% | 23
| V | 2.041 | 28.4% | 22.9
| VI | 2.042 | 28.3% | 22.2 | Manually interpolated s.g. and T against standard data tables.
B07 | I | 2.018 | 24.5% | 22.2 | Manually interpolated s.g. and T against standard data tables.
| II | 2.018 | 25.5% | 22.7
| III | 2.015 | 25.1% | 23
| IV | 2.01 | 24.2% | 22.9
| V | 2.017 | 24.7% | 22.6
| VI | 2.012 | 25.1% | 22.6
B08 | I | 2.001 | 22.7% | 22.2 | Manually interpolated s.g. and T against standard data tables.
| II | 1.996 | 21.5% | 22.4
| III | 1.993 | 21.6% | 22.3
| IV | 1.994 | 22.1% | 22.7
| V | 1.997 | 22.6% | 22.8
| VI | 1.992 | 21.3% | 22.8
B09 | I | 1.952 | 15.1% | 22.3
| II | 1.952 | 15.2% | 22.8
| III | 1.949 | 14.9% | 22.5
| IV | 1.958 | 16.9% | 22.8
| V | 1.954 | 16.2% | 23
| VI | 1.949 | 15.1% | 22.2 | Manually interpolated s.g. and T against standard data tables.
B10 | I | 1.941 | 14.3% | 22.2 | Manually interpolated s.g. and T against standard data tables.
| II | 1.937 | 13.3% | 22.8
| III | 1.946 | 14.6% | 23.4
| IV | 1.943 | 15.8% | 22.6
| V | 1.945 | 15.8% | 22.4
| VI | 1.952 | 15.7% | 22.7
Cells identified in order of electrical series connection, starting with I at positive terminal, ending with VI at negative terminal.
These results were captured by Lawrence Stanton, Lindokuhle Mlele and Yamkela Qokose over 5-6 December 2024.
Baptured in the order of A10-A01, B10-B01 (lowest to highest concentration) with some exceptions.